SECTION ________ - GROUND-SUPPORTED

FLAT-BOTTOM WATER STORAGE TANK

  - GENERAL REQUIREMENTS

  - Scope
The Contractor shall be responsible for all labor, materials and equipment necessary for the design, fabrication, construction, painting, disinfection and testing of a welded carbon steel water storage tank built at grade level on a concrete foundation.  Design and construction of the Water Storage Tank shall conform to all requirements of AWWA D100 Standard for Welded Carbon Steel Tanks for Water Storage, except as modified by the requirements of these contract documents.  The Contractor may use Section 14 of the AWWA D100 as a part of the design.  Tanks designed on this basis must incorporate all the provisions of this section.  The requirements of Section 3 of the AWWA D100 are superseded by any differing requirements of Section 14.

  - Qualification of Manufacturer

    - The design and construction of the Ground-Supported Flat-Bottom Water Storage Tank shall only be undertaken by a Contractor with a minimum of five years experience with tank construction.  The Contractor must be able to demonstrate experience through the design and construction of at least five Ground-Supported Flat-Bottom Water Storage Tanks.  The Contractor shall not subcontract the design or erection of the steel tank.

    - As providing a safe work environment is critical for this project, other contractors, and the community, to be approved to bid on this project, given the complexity, and risk associated with the work, all tank contractors are required to have an Experience Modification Rate (EMR) below 0.75 and a Total Recordable Incident Rate (TRIR) below 2.5 for the last three (3) years. Bidders are required to verify the above requirement by providing with their proposal a statement from their insurance carrier confirming the EMR requirement, and their last three (3) years of OSHA 300 Logs to confirm the TRIR requirement.

  - Submittals
No bid will be considered unless this information is provided with the proposal.

    - A list of five Ground-Supported Flat-Bottom Water Storage Tanks constructed within the last five years, including the Owner, tank capacity and the Engineer.

    - A preliminary drawing of the tank showing major dimensions and plate thickness upon which the bid is based, tank diameter, the high water level and the dimensions of the supporting foundation.

    - A foundation design drawing showing preliminary dimensions and approximate quantities of concrete and reinforcing steel.

  - Standard Specifications
All work on the water storage tank shall fully conform to the requirements of the latest published editions of the following Standard Specifications:

    - AWWA (American Water Works Association) D100 Standard for Welded Carbon Steel Tanks for Water Storage.

    - AWWA D102 - Standard for Painting Steel Water Storage Tanks.

    - AWWA C652 - Standard for Disinfection of Water Storage Facilities.

    - AWS (American Welding Society) D1.1

    - NSF (National Sanitation Foundation) 61 - Materials in contact with Potable Water.

    - Steel Structures Painting Council Manual -  Volume 1 - Good Painting Practice,

    - Steel Structures Painting Council Manual - Volume 2 - Systems and Specifications.

    - ACI 318 - Building Code Requirements for Reinforced Concrete

    - ACI 301 –Specifications for Structural Concrete

  - Tank Details
The tank shall be all-welded construction of the most economical design.  All members of structural steel or of reinforced concrete shall be designed to safely withstand the maximum stresses to which they may be subjected during erection and operation.

    - The minimum operating capacity of the storage tank will be ______ US gallons.

    - The tank diameter will be _____feet.

    - The height of the tank, top of foundation to High Water Level, shall be _____ feet.

    - Top of foundation elevation shall be ______.

    - The existing ground elevation is ______.

    - The finished ground elevation shall be ________.

  - Permits, Easements, Electrical Lines and Utilities
Permits, licenses, airspace authority approval and easements required for the construction of the tank and associated work shall be provided by the Owner.

The site plan or specifications shall clearly indicate the approximate location of all overhead or underground electrical lines and other utilities and piping.  The Owner is responsible for relocating or de-energizing any electrical or utility lines that may interfere with the safe construction of the foundation or structure(s).  In general, no overhead lines, or supports, shall pass or be located within 50 feet of any part of the structure or the footprint of the tank.  A minimum vertical clearance of 15 feet shall be provided along any access routes.

  - Working Drawings
After contract award and prior to construction, the Contractor shall provide engineering drawings and design calculations for the steel tank and the foundation.  Drawings shall show the size and location of all structural components and the foundations along with reinforcement details, the required strength and grade of all materials and the size and arrangement of principle piping and equipment.  The drawings and calculations shall bear the certification of a professional Engineer licensed in the State of ____________. The design coefficients and resultant loads for snow, wind and seismic forces, and the methods of analysis shall be documented.

  - DESIGN

  - General 
The structural design of the storage tank shall conform to the following design standards except as modified or clarified as follows:

    - Foundations – AWWA D100 and ACI 318 – Building Code Requirements for    Reinforced Concrete.

    - Steel Tank - AWWA D100

    - The Contractor may use Section 14 of the AWWA D100 as a part of the design.  Tanks designed on this basis must incorporate all the provisions of this section.  The requirements of Section 3 of the AWWA D100 are superseded by any differing requirements of Section 14.

    - Steel Tank Painting – AWWA D102

  - Environmental Loads – AWWA D100 and ASCE 7

    - Wind Load – Wind pressure shall be determined in accordance with AWWA D100, Section 3.1.4.  Basic wind speed used in the Wind Pressure formula shall be determined using the mapped site location and Figure 1 of AWWA D100.  For tanks located in coastal regions, the Owner’s Engineer shall consider the use of an increased basic wind speed as appropriate.

Basic Wind Speed (BWS) =________ MPH

    - Seismic Load – Seismic loads shall be determined in accordance with AWWA D100, Section 13.

        - Region Dependent Transition Period (TL) =________ (Fig. 19)

        - Site Class ________ (Table 25)

        - MCE Spectral Response Acceleration at 0.2sec (SS) and 1sec (S1) (Fig’s. 5-18)

SS =________

S1 =________

Longitude =________ (at tank center)

Latitude =________ (at tank center)

        - Importance Factor (IE) =________ (Table 24)

    - Snow Load – Snow load shall be determined in accordance with AWWA D100, Section 3.1.3.1.

  - Foundation 
A Geotechnical investigation has been carried out at the site and a copy of the report is included with the Contract Documents.  Recommendations for the foundation and allowable bearing capacities are defined in this report.  The Owner shall retain the services of the Geotechnical consultant to verify the adequacy of the bearing stratum after the Contractor has carried out the excavation and before any concrete or reinforcement is placed.  The concrete foundation shall be designed and constructed by the Contractor based upon the recommendations contained in the Geotechnical report.  The report must provide the allowable soil bearing pressure with appropriate factors of safety, the active and passive earth pressure coefficients, the angle of soil internal friction, its cohesion, unit weight and recommendations for bearing depth and backfill requirements.

  - Steel Tank

    - General  
The materials, design, fabrication, erection, welding, testing and inspection of the steel tank shall be in accordance with the applicable sections of AWWA D100 except as modified in this document.

    - Minimum Plate Thickness 
The minimum thickness for any part of the structure shall be 3/16 inch for parts not in contact with water and 1/4 inch for parts in contact with water.

    - Tank Roof
The tank roof shall be designed as per the project drawings.  All interior lap joints will be sealed by means of caulking or continuous seal welding.  The interior lap joints shall be defined to include roof plate laps.  If roof is supported by rafters, the rafter shall be welded to the roof plates as required structurally.  Any unwelded rafter to plate joints shall be sealed by caulking.  The minimum thickness for roof plates not in contact with water will be 3/16”.

3.01     CONSTRUCTION

  - Concrete Foundation
The foundation shall be designed and constructed to safely and permanently support the structure.  The basis of the foundation construction shall be consistent with the soils investigation data included herein at the end of these specifications.  Appropriate changes to construction schedule and price will be negotiated if, during excavation, soil conditions are encountered which differ from those described in geotechnical report.  The concrete foundation shall be constructed in accordance with ACI 301.  Minimum concrete compressive strength shall be as specified in Section ______, “Cast-In-Place Concrete”.

  - Steel Tank Construction

    - General 
The erection of the steel tank shall comply with the requirements of Section 10 of AWWA D100 except as modified by these documents.

    - Welding   
All field welding shall conform to AWS and Section 10, AWWA D100.   The contractor shall ensure welders or welding operators are qualified in accordance with ASME Section IX or ANSI/AWS B2.1.

    - Fabrication  
All fabrication and shop assembly shall conform to the requirements of AWWA D100, Section 9, Shop Fabrication.

    - Erection

      - Plates subjected to stress by the weight or pressure of the contained liquid shall be assembled and welded in such a manner that the proper curvature of the plates in both directions is maintained.  Plates shall be assembled and welded together by a procedure that will result in a minimum of distortion from weld shrinkage.

      - Joints in bottom of tank shall be continuously lap welded on top side only.  The bottom ring of the tank wall shall be continuously welded to the floor plate both inside and outside.

    - Inspection and Testing

Inspection of shop and field welds shall be in accordance with AWWA D100, Section 11, Inspection and Testing.  All inspection shall be performed prior to interior and exterior field painting.  Radiographic inspection shall be performed by an independent testing agency with all cost included in the Contractor’s bid and paid by the Contractor.

    - Painting and Disinfection

Surface preparation and coating of all steel surfaces shall be in accordance with Section ______ “Coating System for Steel Water Storage Tanks”.

  - ACCESSORIES

  - General 
The following accessories shall be provided in accordance with these specifications.  All items shall be in full conformity with the current applicable OSHA safety regulations and the operating requirements of the structure.

  - Ladders

    - An exterior tank ladder shall be attached to the tank shell extending from approximately 8’ above top of foundation to the top of the shell.

    - Ladder side rails shall be a minimum 3/8 inch by 2 inches with a 16 inch clear spacing.  Rungs shall be not less than 3/4 inch, round or square, spaced at 12 inch centers.  The surface of the rungs shall be knurled, dimpled or otherwise treated to minimize slipping.  Ladders shall be secured to the tank by brackets located at intervals not exceeding 10 feet.  Brackets shall be of sufficient length to provide a minimum distance of 7 inches from the center of the rung to the nearest permanent object behind the ladder.

  - Fall Protection  
Ladders shall be equipped with a fall arrest system meeting OSHA regulations.  The system shall be supplied complete with safety harnesses, locking mechanisms, lanyards and accessories for two persons.

  - Openings

    - Roof Hatches
Provide two access hatches on the roof of the tank.  One hatch shall be 30 inch diameter and allow access from the roof to the interior of the tank.  The hatch will be hinged and equipped with a hasp for locking. The hatch cover shall have a 2 inch downward edge.  The second hatch will be 24 inch diameter and flanged with a removable cover so constructed that an exhaust fan may be connected for ventilation during painting operations.  The openings shall have a minimum 4 inch curb.

    - Tank Vent  
The tank vent shall be centrally located on the tank roof above the maximum weir crest elevation.  The tank vent shall have an intake and relief capacity sufficiently large that excessive pressure or vacuum will not develop during maximum flow rate.  The vent shall be designed, constructed and screened so as to prevent the ingress of wind driven debris, insects, birds and animals.  The vent shall be designed to operate when frosted over or otherwise clogged.  The screens or relief material shall not be damaged by the occurrence and shall return automatically to operating position after the pressure or vacuum is relieved.

    - Shell Access Manhole 
One 30 inch diameter and one 24 inch diameter shell manhole shall be provided near grade level to allow access to the tank interior.  The manholes are to be located 180 degrees apart.  The manhole lid shall be hinged or otherwise self-supported and open outward.

  - Rigging 
A painter’s rail attached to the roof, pipe couplings with plugs in the roof or other attachments that provide complete access for painting shall be furnished.

  - Piping

    - Inlet/Outlet Piping
The vertical inlet/outlet pipe connection to the bottom of the tank shall be a ____inch standard weight carbon steel pipe with appropriate transition to a base elbow of the same diameter.  The vertical pipe shall be attached through the bottom of the tank as near to the shell wall as feasible.  The connection from the piping to the tank floor shall be a watertight connection.

    - Overflow 
The overflow pipe shall be designed to carry the maximum design flow rate of ______GPM.  The ____ inch steel overflow pipe shall have a minimum wall thickness of ¼”.  A suitable weir shall be provided inside the tank with the crest located at High Water Level.  The overflow pipe shall extend from the weir and down the exterior of the tank terminating approximately 1 to 2 feet above grade and discharge onto a concrete splash pad.  The point of discharge shall have a 45 degree bend and be equipped with a stainless steel screen.

  - Identification Plate
A tank identification plate shall be mounted above a shell manhole.  The identification plate shall be corrosion resistant and contain the following information.

    - Tank Contractor

    - Contractor’s project or file number

    - Tank capacity

    - Tank diameter and height to High Water Level

    - Date erected

  - Guarantee

  - The tank Contractor shall guarantee its work for a period of one year from the completion date defined in the contract documents to the extent that it will repair any defects caused by faulty design, workmanship or material furnished under the specifications.  If Contractor is not advised of any defects within 30 days of end of guarantee period, guarantee shall be considered fulfilled and complete.  Defects caused by damaging service conditions such as electrolytic, chemical, abrasive or other damaging service conditions are not covered by this guarantee.

  - All guarantees obtained by the tank Contractor from the manufacturer or installer of paint, equipment or accessories not manufactured by tank Contractor shall be obtained for the benefit of the Purchaser.