SECTION 13___ - COMPOSITE ELEVATED WATER STORAGE TANK

  - GENERAL

  - SUMMARY

    - Work Included
This Section includes the design, construction, testing and commissioning of a Composite Elevated Tank and related work including foundation, painting, electrical and appurtenances.

    - Related Documents
Drawings and the general provisions of this document, including General Conditions, Supplemental Conditions, Special Provisions and other Sections apply to work in this Section.

  - REFERENCES:  The following Specifications, Codes and Standards may be referenced in this Section.  All references are to the latest published edition.

    - American Concrete Institute (ACI)
117-10	Standard Tolerances for Concrete Construction and Materials 
228.1R-03	In-Place Methods to Estimate Concrete Strength 
301-05	Specification for Structural Concrete 
304-00	Guide for Measuring, Mixing, Transporting and Placing Concrete
305-10	Hot Weather Concreting
306-10	Cold Weather Concreting
318-08	Building Code Requirements for Structural Concrete
347-04	Guide to Formwork for Concrete
371R-08	Guide for the Analysis, Design and Construction of Elevated 
	Concrete and Composite Steel-Concrete Water Storage Tanks

    - American Institute of Steel Construction (AISC)
S335	Specification for Structural Steel Buildings

    - American National Standards Institute (ANSI)
B16.5	Pipe Flanges and Flanged Fittings

    - American Society of Civil Engineers (ASCE)
ASCE 7	Minimum Design Loads for Buildings and Other Structures

    - American Society for Testing Materials (ASTM)
A 123 	Zinc Coatings on Iron and Steel Products
A 240	Stainless Steel Plate, Sheet and Strip for Pressure Vessels
A 285	Pressure Vessel Plates, Carbon Steel
A 774	Welded Stainless Steel Fittings
A 778	Welded Stainless Steel Tubular Products

    - American Water Works Association (AWWA)
C652-11	Disinfection of Water-Storage Facilities
D100-11	Welded Steel Tanks for Water Storage
D102-11	Coating Steel Water Storage Tanks
D107-10	Composite Elevated Tanks for Water Storage

    - Federal Aviation Administration (FAA)
70/7460-1H	Obstruction Marking and Lighting

    - National Association of Corrosion Engineers (NACE)
RP0178	Recommended Practice - Fabrication Details, Surface Finish 
	Requirements and Proper Design Considerations for Tanks and
	Vessels to be Lined for Immersion Service

    - National Fire Protection Association (NFPA)
NEC	National Electric Code
780	Standard for the Installation of Lightning Protection Systems

    - National Sanitation Foundation (NSF)
61	Standard for Drinking Water System Components

    - Occupational Safety and Health Administration (OSHA)
29 CFR Part 1926	Safety and Health Regulations for Construction

    - Steel Structures Painting Council (SSPC)
VIS-89	 Visual Standard for Abrasive Blast Cleaned Steel

  - SYSTEM DESCRIPTION

    - Elevated Tank
The Composite Elevated Tank shall consist of the following: foundation, reinforced concrete support structure and a welded steel water tank.  The support tower shall extend vertically from the foundation as a circular concrete support structure/wall.  A structural concrete dome shall be provided as structural support for the contained water within the perimeter of the wall.  A reinforced concrete ring beam shall be provided to connect the welded steel water tank, concrete dome and concrete support wall.  The Composite Elevated Tank shall be in accordance with the shape, dimensions and details required by these                      Specifications and Drawings.  Dimensions may be slightly adjusted to suit the Composite Elevated Tank Manufacturer’s standard welded steel water tank shape.

    - Operating Parameters
Minimum capacity within operating range	________ gallons
Maximum operating range			________ ft.
Elevation	- overflow/top capacity	________ ft.
  		- grade slab			________ ft.
 		- final grade			________ ft.

    - General Design
Design Standards
The structural design of the Composite Elevated Water Storage Tank shall conform to AWWA D107 and the following design standards.  In case of conflict between the Standard and the criteria listed below, the more stringent requirement shall apply.

Reinforced Concrete Foundation - ACI 318
Concrete Support Structure – AWWA D107 and ACI 318
Welded Steel Water Tank - AWWA D107

    - Environmental Loads – AWWA D107and ASCE 7

      - Wind Load – Wind pressure shall be determined in accordance with AWWA D107, Section 4.2.6.  Basic wind speed used in the Wind Pressure formula shall be determined using the mapped site location and Figure 2 of AWWA D107.  For tanks located in coastal regions, the Owner’s Engineer shall consider the use of an increased basic wind speed as appropriate.

Basic Wind Speed (BWS) =________ MPH

      - Seismic Load – Seismic loads shall be determined in accordance with AWWA D107, Section 4.2.8.Seismic design criteria shall be determined in accordance with AWWA D107, Section 4.2.7.

        - Region Dependent Transition Period (TL) =________ (Fig. 1)

        - Site Class ________ (Table 3)

        - MCE Spectral Response Acceleration at 0.2sec (SS) and 1sec (S1) (Fig’s. 3-16)

SS =________

S1 =________

Longitude =________ (at tank center)

Latitude =________ (at tank center)

        - Importance Factor (I) =________ (Sec. 4.2.7.7)

      - Snow Load – Snow load shall be determined in accordance with AWWA D107, Section 4.2.5 (20 psf minimum loading).

    - Foundation Design – AWWA D107
The foundation shall be designed by the Composite Elevated Water Storage Tank Contractor to safely support the structure based on the foundation recommendations within the geotechnical consultant’s soil report (See also 1.7.2).  Foundations shall be sized in accordance with load combinations defined by AWWA D-107, Sec. 4.3

  - SUBMITTALS

    - Proposal (Submit the following with the proposal):

      - Experience List - A completed contracts summary shall demonstrate a minimum of ten years experience in the design and construction of Composite Elevated Tanks.  Contractor shall list a minimum of five completed Composite Elevated Tanks of similar capacity.  Provide the location, capacity, Owner’s name and contact information, Engineer’s name and contact information and year completed.  Failure to provide this information shall be cause for rejection of the bid (See also 1.5.1).

      - Tank Drawing - A preliminary section view drawing of each sized Composite Elevated Tank proposed for this project.  The drawing shall include sufficient detail to illustrate tank geometry, materials of construction, primary dimensions, the high water level elevation, concrete support structure wall thickness and other information required to show compliance with this Specification.  If the proposed design does not comply with this Specification, the bid shall be cause for rejection of the bid.

      - Foundation Drawing – A drawing of the preliminary design of the foundation for each sized Composite Elevated Tank proposed for this project.  The drawing shall include sufficient detail to illustrate foundation geometry, materials of construction, preliminary dimensions and approximate quantities of concrete and reinforcing steel.  Failure to provide this information shall be cause for rejection of the bid.

    - Construction Drawings

      - Provide elevation, plan and sectional view drawings of the foundation, concrete support structure, welded steel water tank and all appurtenant equipment and accessories.  Show the location, dimensions, material specifications and finish requirements.  The submission shall be sealed by a professional engineer registered in the State of ________.

      - Reinforced concrete details shall include construction joints, openings and inserts.  Reinforcement shall be clearly indicated on the structural drawings and identified by mark numbers that are used on the fabrication schedule.  Location, spacing and splice dimensions shall also be shown.  Placement and fabrication details shall conform to ACI 318.

      - Steel tank details shall include weld joints and a layout showing all primary and secondary shop and field welds.

    - Construction Procedures

      - Provide design, detail drawings and procedures for the support structure forming system.  Details shall include location of form and construction joints, rustications and any form ties.  The criteria and minimum elapsed time for adjacent concrete placement shall also be clearly stated in the construction procedures.  Procedures shall yield a minimum of twenty-four (24) hours of cure time before form removal (See also 3.2.2).

      - Provide shop and field weld procedures for all structural joints on the steel tank.

    - Design Data

      - Provide a table showing capacity of the tank in gallons at all levels in one ft. increments.

      - Provide a summary of the design for the foundation, concrete support structure, welded steel water tank and other components.  Include the design basis, the loads and load combinations and the results.

    - Product Data

      - Provide separate concrete mix designs for each specified concrete compressive strength indicated on the drawings.

      - Provide technical data and manufacturer’s standard color chart of all coating products to be used.

      - Provide manufacturer’s descriptive information for appurtenant equipment and accessories that are not detailed on the construction drawings.

    - Reports/Certification

      - Provide documentation of all tests, inspections and certifications required by this Section.

      - Provide general qualifications of all welders.

    - Operation/Maintenance
Provide operating instructions and maintenance procedures for the Composite Elevated Tank and applicable appurtenant equipment, mechanical components and miscellaneous accessories.

  - QUALITY ASSURANCE

    - Qualification of Manufacturer

      - A turnkey Composite Elevated Tank Manufacturer/Contractor shall perform the work described in this Section.  No part of the design or construction of the concrete support structure or welded steel water tank shall be subcontracted.  The Contractor shall have designed, constructed and placed in service a minimum of five (5) Composite Elevated Tanks of similar capacity in the past ten (10) years.

      - The Contractor shall employ a full-time Professional Engineer with a minimum five (5) years cumulative experience in the design and construction of Composite Elevated Tanks.  The engineer shall be registered in accordance with these specifications and shall be in responsible charge of the work.

      - The Contractor shall own and maintain all equipment necessary for the turnkey construction of the Composite Elevated Tank as specified herein.  This includes the formwork for the concrete support structure construction as well as the fabrication and erection equipment required for the welded steel water tank construction.  Neither the concrete support structure construction or the welded steel water tank fabrication and erection shall be subcontracted.

      - As providing a safe work environment is critical for this project, other contractors, and the community, to be approved to bid on this project, given the complexity, and risk associated with the work, all tank contractors are required to have an Experience Modification Rate (EMR) below 0.75 and a Total Recordable Incident Rate (TRIR) below 2.5 for the last three (3) years. Bidders are required to verify the above requirement by providing with their proposal a statement from their insurance carrier confirming the EMR requirement, and their last three (3) years of OSHA 300 Logs to confirm the TRIR requirement.

    - Regulatory Requirements

      - The Specifications, Codes and Standards referenced in paragraph 1.2 shall govern the work with regard to materials, design, construction, inspection and testing to the extent specified.

      - The Composite Elevated Tank shall be designed and constructed in compliance with applicable federal, state and local regulations.

      - Personnel safety equipment shall be provided in accordance with OSHA requirements and the manufacturers’ documentation.

  - DELIVERY, STORAGE, & HANDLING

    - Handling and Shipping
The Contractor shall handle materials and fabricated components in a manner that will protect them from damage.  Allow painted materials adequate cure time prior to stacking or shipping.

    - Storage and Protection
Protect delivered materials and equipment from damage.  Store in well drained areas and provide blocking to minimize contact with the ground.

  - PROJECT CONDITIONS

    - Permits and Easements

      - Permits, licenses and easements required for permanent structures, changes in existing facilities or necessary advancement of the specified construction shall be secured and paid for by the Owner prior to the start of construction.  These include building permits, airspace authority approval, site access easements, highway crossing permits, etc.

      - Licenses or permits of a temporary nature required by specific trades shall be the responsibility of the Contractor.

    - Existing Conditions
A geotechnical consultant has carried out a soils investigation at the site and a soil report has been incorporated within these specifications.  The net allowable bearing pressure of shallow foundation and/or the allowable capacity of deep foundation elements have been defined in this report.  The Contractor shall be responsible for securing any further geotechnical information required beyond that provided in this report.  The Owner shall retain the services of the Geotechnical consultant to verify the adequacy of the bearing stratum after the Contractor has carried out the excavation and before any concrete or reinforcement is placed.

    - Access
The Contractor shall provide access from public roads to the tank site unless otherwise specified.

    - Working Conditions

      - Safety and Health - The Contractor shall comply with safe working practices and all health and safety regulations of OSHA, state and local health regulatory agencies and Material Safety Data Sheets (MSDS).  Provide protective and lifesaving equipment for persons working at the site.

      - Times for Work - Times for work shall comply with local, state and federal regulations and laws.

  - SEQUENCING AND SCHEDULING

    - Schedule
The Contractor shall provide an anticipated schedule for design, submittals, site work and the major components of construction including foundation, concrete support structure and welded steel water tank, tank painting, electrical installation and other significant activities.  Update the schedule as required.

    - Notification
The Contractor shall provide notification of the intent to start work at least seven days prior to commencing each major phase of work.

    - Certifications

      - Provide certification from the Engineer of Record that the Composite Elevated Tank has been completely designed in accordance with the requirements of the Specification.

      - Provide certification that field testing and inspection requirements of item 3.4 have been performed and the results comply with the requirements of the specification.

  - GUARANTEES

    - The Contractor shall guarantee the structure, appurtenant equipment and accessories provided under this Section against defective design, workmanship, or materials for a period of one year from the date of substantial completion.  If notified within this period, the Contractor shall repair any defects caused by faulty design, workmanship, or material furnished under these specifications at no cost to the Owner.  If Contractor is not advised of any defects within 30 days of the end of the guarantee period, then this guarantee shall be considered fulfilled and complete.  Defects caused by damaging service conditions, such as electrolytic, chemical, or abrasive, are not covered by this guarantee.

    - All guarantees from any manufacturer or installer of paint, materials, equipment and accessories not manufactured by the Composite Elevated Tank manufacturer and that are provided under this Section, shall be obtained by the Contractor and submitted to the Owner.

2.01     PRODUCTS

  - MATERIALS

    - Reinforced Concrete
Concrete materials and reinforcement shall comply with ACI 318 and AWWA D107, except as modified in this Section.

    - Steel Tank
Welded steel water tank components, including steel plates, sheets, structural shapes and filler metals shall be in accordance with AWWA D107,.

  - CONCRETE FOUNDATION
The concrete foundation shall be designed in accordance with ACI 318.  Minimum specified compressive strength shall be 4000 psi at 28 days.  Reinforcing steel shall be ASTM A615 Grade 60.  The service load reinforcement tension stress shall not exceed 30,000 psi under dead plus water load unless flexural cracking is otherwise controlled in accordance with ACI 318.

  - CONCRETE SUPPORT STRUCTURE
The concrete support structure shall be designed in accordance with ACI 318.  The specified compressive strength of concrete shall be as required by design, but not less than 4000 psi at 28 days.  The maximum specified compressive strength of concrete for the wall and dome shall be 6000 and 5000 psi respectively.

    - Support Wall
The support wall shall be reinforced concrete with a minimum thickness of 8 in. exclusive of any architectural relief.  Wall thickness shall be provided such that the average compressive stress due to the weight of the structure and stored water is limited to 25% of specified compressive strength, but not greater than 1000 psi.  A minimum total wall reinforcement of 0.15% vertically and 0.20% horizontally shall be distributed approximately equally to each face. A minimum of 0.75% vertical reinforcement shall be provided in the top 6 ft. of the wall extending into the concrete ring beam. Minimum concrete cover for interior/exterior faces shall be 1 in. and 1-1/2 in. respectively.

    - Tank Floor
The tank floor shall be a reinforced concrete dome not less than 8 in. thick.  The average compressive stress due to the weight of the structure and stored water shall not exceed 15% of the specified compressive strength, nor greater than 600 psi.  Minimum total reinforcement in orthogonal directions shall be 0.40% distributed approximately equally to each face.  Additional reinforcement shall be provided for stress caused by edge restraint effects.

    - Openings

      - The effects of openings in the wall shall be considered in the design.  Not less than 60% of the interrupted reinforcement in each direction shall be placed each side of the opening.  Reinforcement shall extend past the opening not less than half the transverse opening dimension.

      - Openings 8 ft. 0 in. or wider used for vehicle access shall be strengthened against vehicle impact and local buckling by means of an internal buttress located on each side of the opening.  The buttress shall consist of a thickened, reinforced concrete wall section that is integrally formed and placed with the concrete support structure.

  - CONCRETE SUPPORT STRUCTURE/STEEL TANK INTERFACE

    - Interface Region

      - The interface region includes those portions of the concrete support structure and steel tank affected by the transfer of forces from the tank cone and the tank floor to the concrete support structure.  This includes a ring beam and connection details.  The Contractor shall provide evidence that a thorough review of the interface region has been performed.  Finite element and finite difference analyses are the required methods for examining such local stresses in detail.

      - The geometry of the interface shall provide for positive drainage and not allow either condensate or precipitation to accumulate at the top of the concrete wall or ring beam.

    - Ring Beam

      - The ring beam shall be reinforced concrete with a nominal width and height of at least two times the concrete support structure wall thickness. Minimum radial and circumferential reinforcement shall be 0.25%.  For direct tension, reinforcement shall be provided such that the average service load stress in tension reinforcement due to the weight of the structure and stored water does not exceed 12,750 psi.

      - Ring beam design shall consider unbalanced forces from the welded steel tank cone and concrete dome, load conditions varying with water level, eccentricity of loads resulting from design geometry and allowance for variations due to construction imperfection and tolerance.

  - WELDED STEEL TANK

    - General
The steel tank shall be all welded construction and shall be designed, fabricated and erected in accordance with applicable sections of AWWA D107.  The required capacity and dimensions of the tank are noted on the drawings and in this Section of the specifications.  All exposed lap joints shall be fully seal welded on both sides.

    - Plate Thickness
All members shall be designed to safely withstand the maximum stress to which they may be subjected during erection and normal operation.  The minimum thickness of any steel plate in contact with water shall be 1/4 in.  The minimum thickness of any steel plate not in contact with water shall be 3/16 in.

    - Roof Support
All structural members supporting the roof of the steel tank shall be flat bar or sealed square tubular sections.  I-beams or other sections with horizontal projections may be used if the nominal depth is 10 in. or greater.  Support beams shall be seal welded to the underside of the roof plate along the entire length of the beam.

    - Cone
Conical sections of the tank shall be designed using one of the 3 methods described in AWWA D107, Section 5.3.5.  Inspections and reports shall be provided to the extent required by AWWA D107.

    - Bottom Liner
Liner plates shall be shop fabricated to conform to the shape of the concrete dome.  They may be placed directly on the concrete.  All liner plate seams shall be lap welded on the topside only with continuous fillet welds or continuous butt welds with backup bars.  The minimum thickness for liner plates shall be 1/4 in.

  - APPURTENANCES AND ACCESSORIES

    - General
Accessories shall comply with the minimum requirements of the Specifications, Codes and Standards listed in paragraph 1.2, current applicable safety regulations and the operating requirements of the structure.

    - Ladder Access

      - Ladders shall be provided from the slab on grade inside the base of the concrete support structure to the upper walkway platform located below the tank floor.  The tank floor manhole shall be provided with ladder access from the upper platform.  A ladder shall extend from the upper platform, through the access tube interior to the roof.  A ladder mounted on the access tube exterior shall be provided for access to the tank interior, extending from the roof manhole to the tank floor.

      - Ladders that terminate at platforms or landings shall extend 48 in. above the platform elevations.  A removable extension kit (Bilco Ladder-Up Safety Post or equal) shall be added to the fall protection system for all ladders not extending 48 in. above the platform elevations.

      - Ladders located in the concrete support structure shall be galvanized steel.  Tank interior and access tube ladders shall be coated in accordance with the tank interior coating system.

      - Ladder side rails shall be a minimum 3/8 in. by 2 in. with a 16 in. clear spacing.  Rungs shall be minimum 3/4 in. diameter, spaced at 12 in. centers and plug welded into holes drilled in the side rails.  The surface of the rungs shall be knurled, dimpled, or otherwise treated to minimize slipping.

      - Ladders shall be secured to the adjacent structure by brackets located at intervals not exceeding 10 ft.  Brackets shall be of sufficient length to provide a minimum distance of 7 in. from the center of the rung to the nearest permanent object behind the ladder.  Ladder brackets located on the access tube exterior shall be reinforced at the access tube shell so that potential ice damage is confined to the ladder and bracket; and not the access tube shell.

    - Safe Climbing Device/Safety Equipment
OSHA compliant safe climbing system shall be provided on all ladders.  Two sleeves with snap hooks shall be provided that are designed to be operated with the system.  Two harnesses with shock resistant lanyards shall be provided with the system.

    - Rest Platforms (optional)
Rest platforms shall be provided at maximum 50 ft. intervals along the interior concrete support structure ladder. The platforms shall be nominal 5 ft. x 5 ft. and platform floor shall be grating.  Openings shall be provided in the landings to accommodate the ladder that shall have a straight-run its full height. All platform components shall be galvanized steel and attachment hardware shall be zinc plated.

    - Platforms
A 4 ft. wide upper walkway platform shall be located at the top of the concrete support structure to provide access from the concrete support structure ladder to the roof access ladder located on the interior of the access tube.  Platforms shall be provided with handrails, midrails and toe plates in accordance with OSHA requirements.  Grating shall be used for the walking surface.  All components shall be galvanized steel and attachment hardware shall be zinc plated.

    - Concrete Support Structure Doors

      - Personnel Door - Door frames shall be 16-gauge with concealed reinforcement at hardware locations.  Expansion type anchors for existing openings shall be installed near the top, bottom and intermediate point of each jamb to rigidly secure the frame.  Doors shall be 1-3/4 in. thick insulated, reinforced, full, flush type with 18-gauge face sheets and concealed reinforcement at hardware locations.  All edges shall be finished flush with watertight seams.  Shop applied finish for the frame and door shall be baked on rust inhibitive primer.  Field finish shall be compatible with the tank exterior.  Standard hardware shall be stainless steel and include three 4-1/2 in. by 4-1/2 in. hinges, industrial duty closer and lockset.  Quantity, location and size of personnel door(s) shall be as shown on the Project Drawings.

      - Overhead Vehicle Door
Provide a manually operated ________ (10 ft. x 10 ft. is standard) overhead steel rolling door located in the base of the tower.  The door frame shall be fabricated of galvanized steel plate, fastened and reinforced on the interior face of the concrete support structure.  The curtain shall be formed of 22-gauge steel interlocking slats designed for a wind loading of 20 psf.  A 24-gauge steel hood shall be provided with a weather seal to protect the assembly.  The curtain, bottom bar, brackets, guides, hood, pipe and chain shall be galvanized.  Size and location of the overhead door shall be as indicated on the project drawings.

    - Tank Openings

      - Floor - Provide a 30 in. diameter manhole through the tank floor.  The manhole shall be operable from a ladder located on the upper platform and shall be designed to withstand the pressure of the tank contents without leakage.  The manhole assembly shall include a stainless steel hand wheel operator and threaded components.

      - Roof - Provide one 30 in. diameter weatherproof access hatch on the roof of the tank.  The hatch will allow access from the roof to the interior tank ladder.  The hatch opening shall have a minimum 4 in. curb.  Hatch cover to be constructed of aluminum and shall have a 2 in. downward edge, stainless steel hardware and locking mechanism.

      - Roof – Provide one 24 in. diameter exhaust hatch located adjacent to the roof hatch.  The exhaust hatch will be flanged with a bolted removable cover and designed such that an exhaust fan may be connected for ventilation during painting.  The opening shall have a minimum 4 in. curb.

    - Access Tube

      - Provide a ________ in. (Consider the extra size requirements of running cabling or future antennae connections thru this access tube.) diameter centrally located access tube through the welded steel water tank to provide access to the tank roof from the upper walkway platform.  A 30 in. diameter access hatch shall allow egress from the access tube to the roof.  The openings shall have a minimum 4 in. curb.  Hatch cover to be constructed of aluminum and shall have a 2 in. downward edge, stainless steel hardware and locking mechanism.

      - The area under the access tube shall be provided with a galvanized drip pan to prevent condensation from dripping onto the concrete floor slab below.  The drip pan shall extend 3 in. beyond the drip line of the access tube.  A 3/4 in. PVC drain pipe shall be provided to drain condensate to the overflow.

    - Roof Railing (optional)
A 42 in. high roof handrail shall be provided to enclose all centrally located roof accessories.  The roof railing shall be a minimum of 15 ft. diameter.

    - Rigging Access
A removable access panel shall be located at the top of the concrete support structure accessible from a platform and shall provide access to the exterior rigging rails located near the welded steel tank/concrete support structure interface.  This access panel shall be stainless steel or aluminum and have a minimum size of 24 in. by 36 in.  In most cases, this removable access panel serves as one of the concrete support structure vents (See also 2.6.13.2).

    - Utility Rails
Provide permanently installed utility rails suitable for rolling trolleys on the interior of the welded steel tank at the wall/roof and access tube/roof connections.  Provide an exterior utility rail at the base of the welded steel tank adjacent to the concrete support structure.  Provide an interior concrete support structure utility rail at the top of the concrete support structure in order to assure access for maintenance of piping.

    - Piping

      - Inlet/Outlet Pipe - Provide a ________ in. diameter inlet/outlet pipe that extends from the base of the concrete support structure thru the floor elevation of the welded steel tank.  Provide a minimum of 6 in. high removable silt stop where the inlet/outlet pipe enters the tank.  The bottom capacity level of the tank's operating range shall be at or above the elevation of the top of the silt stop.  Pipe material within the concrete support structure shall be minimum 10-gauge 304L stainless steel.

The inlet/outlet pipe shall be designed to support all related static and dynamic loads.  Suitable galvanized brackets, guides and hangers shall be provided on the wall of the concrete support structure and welded steel water tank floor at intervals not exceeding 20 ft.  

The inlet/outlet pipe shall be designed and constructed to accommodate any differential movement caused by settlement and by thermal expansion and contraction over the range of extreme temperature differences expected for the concrete support structure and pipe.  The required flexibility shall be provided by an expansion joint located in the vertical section of pipe.

      - Overflow Pipe - Provide a ________ in. diameter overflow pipe.  The top of the overflow shall be located within the welded steel water tank at the overflow elevation.  The overflow pipe shall be routed beside or inside the central access tube and extend to grade inside the concrete support structure.  A base elbow shall direct the overflow through the wall of the concrete support structure, where the pipe shall be terminated with a No. 4 mesh screen.  Pipe material within the support structure shall be minimum 10-gauge 304L stainless steel.  If the top of the overflow pipe is located above top capacity level, the tank shall be designed for the additional capacity provided by the difference.

The entrance to the overflow pipe shall be designed for the maximum inlet flow rate.  The design shall be based on the water level cresting within 6 in. above the overflow elevation.  A weir shall be provided if the entrance capacity of the overflow pipe diameter is not adequate.  The Contractor’s standard vortex prevention device shall also be used.

The overflow shall be designed to support all related static and dynamic loads.  Suitable galvanized brackets, guides and hangers shall be provided on the wall of the concrete support structure and welded steel water tank floor at intervals not exceeding 20 ft.  The overflow and weir section within the tank shall be coated carbon steel and supported by the central access tube.

The overflow pipe shall be designed and constructed to accommodate any differential movement caused by settlement and by thermal expansion and contraction over the range of extreme temperature differences expected for the concrete support structure and pipe.  The required flexibility shall be provided by an expansion joint located in the vertical section of pipe.

      - Stainless Steel Requirements - Pipe and fittings shall be Type 304L stainless steel fabricated from material meeting the requirements of ASTM A240.  Fabrication, inspection, testing, marking and certification of pipe and fittings shall be in accordance with ASTM A778 and A774, respectively.  Backing flanges shall be in accordance with ASTM A285-C drilled to ANSI B16.5 Class 150.

Pipe, fittings and flange thickness shall be in accordance with the manufacturers certified pressure rating for the applicable service pressures.

    - Ventilation

      - Tank Ventilation - A tank vent shall be provided, located near the center on the tank roof above the maximum weir crest elevation.  It shall consist of a support frame, screened area and cap.  The support shall be fastened to a flanged opening in the tank roof.  The vent cap shall be provided with sufficient overhang to prevent the entrance of wind driven debris and precipitation.  A minimum of 4 in. shall be provided between the roof surface and the vent cap.

The tank vent shall have an intake and relief capacity sized to prevent excessive pressure differential during the maximum flow rate of water, either entering or leaving the tank.  The overflow pipe will not be considered as a vent.  The maximum flow rate of water exiting the tank shall be calculated assuming a break in the inlet/outlet at grade when the tank is full.  The vent shall be provided with an insect screen.  Vent capacity shall be determined based on open area provided by the screen.

      - Support Structure Ventilation - As a minimum, one louvered vent shall be provided at the top of the concrete support structure.  This vent shall be accessible from the upper platform and may also be designed to provide access to the exterior rigging rails located at the welded steel tank/concrete support structure intersection.  Vents shall be galvanized steel with stainless steel or aluminum insect screen.

    - Interior Floors

      - Slab on Grade - Provide a 6 in. thick, 3500 psi concrete floor slab in the base of the concrete support structure.  The slab shall be supported on compacted granular fill and shall be reinforced with #5 reinforcing steel bars at 12 in. centers each way.  Provide 1/2 in. expansion joint between floor slab and concrete support structure and at pipes and supports that extend through the floor.  Place cap strip and sealant over the expansion joint.  The slab shall be sloped at 0.5% toward the overhead door for drainage.

    - Lightning Protection

      - Provide a lightning protection system for the Composite Elevated Tank and any roof mounted equipment that may be damaged by lightning.  Install the system in accordance with NFPA 780 with materials that meet UL96 and UL96a.

      - Minimum requirements include two 28 strand by 14-gauge copper conductors bonded to the steel tank 180 degrees apart. The conductors shall be fastened to the interior concrete support structure at 3 ft. minimum spacing and shall terminate with buried 5/8 in. diameter by 8 ft. long copper clad ground rods.

    - Identification Plate

      - A tank identification plate shall be mounted near the personnel door.  The identification plate shall be corrosion resistant and contain the following information:

        - Tank Contractor

        - Contractor’s project or file number

        - Tank capacity

        - Height to High Water Level

        - Date erected

  - ELECTRICAL AND LIGHTING
Refer to Section ________ of the Project Specifications.

  - STEEL TANK PAINTING
Refer to Section ________ of the Project Specifications.

  - SOURCE QUALITY CONTROL

    - Tests
Review mill test certifications of all steel plate, structural components and reinforcement to ensure compliance with specification requirements.

    - Quality Assurance
Provide quality assurance of shop fabricated components in accordance with AWWA D100.

3.01    EXECUTION

  - EXAMINATION

    - Foundation Excavation
The foundation bearing surface and excavation shall be inspected and verified by a geotechnical engineer retained by the Owner prior to construction of the foundation (See also 1.7.2).

    - Environmental Conditions
Prior to performing any work, verify the expected temperature, humidity and weather conditions are within the specified limitations for executing the work.

    - Elevated Tank Components
After completion of each major component and prior to proceeding with the next stage of construction, verify that tolerance inspections and material quality control tests conform to this specification.

  - REINFORCED CONCRETE CONSTRUCTION

    - Reinforcement

      - Fabrication, placement, development and splicing of reinforcement shall be in accordance with ACI 318 and ACI 117.

      - Concrete support structure reinforcement shall be installed with plastic supports.  Maximum spacing of supports for welded wire fabric shall be 5 ft. centers, horizontal and vertically.

    - Architectural Concrete Construction (Concrete Support Structure or Pedestal Shaft)

      - The exposed exterior surface of the concrete support structure is designated as architectural concrete. The concrete and formwork requirements of this Section shall be strictly enforced to ensure concrete of the highest practicable structural and architectural standard. Concrete proportioning, placing and finishing shall be in accordance with the ACI 301, Chapter 18, except as modified by this Section. Formwork design, installation and removal shall comply with the minimum requirements of ACI 318 and ACI 117 and with the applicable requirements of ACI 347 and ACI 371R, except as modified by this Section.

      - Attention shall be given to ensure the same concrete design mix is used throughout the concrete support structure. The proportion, type and source of cement and aggregates shall not be changed. Uniform moisture content and placing consistency shall be maintained.

      - Drop chutes shall be used in all wall concreting operations where concrete placement is 5 ft. and greater in drop height. Concrete shall be placed directly between reinforcement layers to prevent aggregate segregation and form splatter with the resulting finish variations.

      - Forming systems not designed for lateral pressures associated with full height plastic concrete head shall be designed with the provision of ties and bracing such that concrete components conform to the correct dimensions, shape, alignment and elevation without leakage of mortar.  Formwork systems shall be designed to safely support all loading conditions.  Embedded items shall be properly positioned and secured.  Form surfaces shall be cleaned of foreign materials and coated with a release agent prior to placing reinforcement. Do not allow excessive release agent to accumulate on the form.  Steel forms shall be coated with non-staining, rust preventative form oil or otherwise protected.

      - The forming system for the concrete support structure wall shall be fully engineered and detailed with procedures to meet the increased demands of architectural concrete. The concrete support structure shall be constructed with a jump form process using form segments prefabricated to match the wall curvature.  Concrete pour height shall be a minimum of 4 ft. and a maximum of 12 ft.  Form panels shall extend the full height of the concrete pour using only vertical panel joints. Form systems that are designed to lap the previous wall pour shall be sealed to prevent grout leakage. Form system shall incorporate a positive means of adjustment to maintain dimensional tolerances specified herein.  Panels shall be designed for lateral pressures associated with full height plastic concrete head; support and bracing shall be provided for construction related impact loads and wind loads.  Working platforms that allow safe access for inspection and concrete placement shall be provided.  Form facing material shall be metal, or plywood faced with plastic or fiberglass.

      - The form system shall incorporate a uniform pattern of vertical and horizontal rustications to provide architectural relief to the exterior wall surface.  Rustication strips shall be attached to the form face to minimize potential grout leakage that results in broken corners, color variations and rock pockets.  All construction joints and panel joints shall be located in rustications.  Vertical panel joints shall be sealed using closures that combine with the form pattern to prevent grout leakage and panel joint lines. All joints shall be grout tight in order to prevent leakage during concrete placement.  The vertical and horizontal rustications shall be proportioned and combined to impart a symmetrical architectural pattern to the completed structure.  No architectural form treatment is required on the interior surface.

      - Support structure concreting shall be capable of segmented placement procedures only when required.  Temporary vertical bulkheads shall divide the wall pour into segments corresponding to a single batch (truckload) of concrete.  The bulkheads shall be located at rustications; braced rigid and tight to maintain vertical alignment under concrete load without grout leakage.  Wall segment concrete shall be placed continuously to full form height from a single load.  Placement from multiple batches is not permitted.  Temporary bulkheads shall not be removed until adjacent concrete is placed.

      - Wall forms shall not be disturbed or removed for a minimum period of twenty four (24) hours after concrete placement.  Additionally, in no instance shall the forms be removed before the concrete has attained sufficient strength to prevent forming operations or environmental loads from causing surface damage or excessive stress.  Form removal shall be based on early age concrete strength testing.  The minimum concrete strength shall be established by the Contractor, based on an analysis of stress at critical stages throughout the forming and concrete operations.  Early age concrete testing shall be in accordance with ACI 228.1R-03.

      - The formwork system for the domed structural floor shall be designed to support all construction loads.  Adequate shoring and bracing shall be provided to transfer loads without appreciable movements.  Form surfaces shall be steel, plastic, or fiberglass coated material.  Shoring and forms for the structural dome slab shall remain in place until the concrete has gained sufficient strength to carry the floor weight without damaging deflections.

    - Concrete
Concrete proportioning, production, placement, quality control and curing procedures shall comply with ACI 318 and ACI 117.  Concrete shall satisfy the specific structural, durability and architectural requirements of the completed components.

      - Proportioning - The proportions of materials for concrete shall be established to provide adequate workability and proper consistency to permit concrete to be worked readily into the forms and around reinforcement without excessive segregation or bleeding.  If high range water reducer is used, concrete slump prior to addition shall be 3 to 4 in.  The slump, after addition of high range water reducer, shall be a maximum of 9 in.  Air shall be entrained to provide concrete with 3.5% to 6.5% air content.

      - Production - Concrete that arrives at the project with slump below that suitable for placing may have water added within the limits of the maximum permissible water-cement ratio.  Maximum slump shall not be exceeded.  The water shall be incorporated by additional mixing equal to at least half of the total mixing time required.  For concrete with site-administered high range water reducer, the preplasticized minimum slump requirement shall be attained as permissible by addition of water and mixing prior to the addition of the water reducer.

      - Placement - Prior to concrete placement, all snow, ice, water, or other foreign material shall be removed from the spaces that the concrete will occupy.  Concrete shall be deposited in its final position in accordance with ACI 318 or the applicable building code.  Drop chutes or tremies shall be used in walls and columns to prevent free-fall of the concrete over 5 ft. and to allow the concrete to be placed through the cage of reinforcing steel.  These shall be moved at short intervals to prevent stacking of concrete.

      - Vibration - All concrete shall be consolidated by vibration so that the concrete is thoroughly worked into the corners of forms and around the reinforcement and embedded items to eliminate all air or stone pockets which may cause honeycombing.  Internal vibrators shall be the largest practical size that can be used in the work and shall be operated by competent workmen.

      - Wall Finish - Provide a smooth form finish for the interior and exterior concrete support structure.  Tie holes shall be plugged using grout on the interior and manufactured plugs on the exterior that match the color of the cured concrete as closely as possible.

      - Dome Finish - Provide a smooth form finish for the interior dome slab.  The unformed surface shall have a floated finish.

    - Weather

      - Concrete shall not be placed during precipitation or extreme temperatures unless protection is provided.

      - During cold weather the recommendations of ACI 306 shall be followed.

      - During hot weather the recommendations of ACI 305 shall be followed.

    - Concrete Support Structure Dimensional Tolerances
Support structure concrete construction shall conform to the following:

- Variation in thickness
Wall	-3.0% to +5.0%
Dome	-6.0% to +10.0%

- Concrete support structure variation from plumb:
in any 10 ft. of height		-	1 in.
in any 50 ft. of height		-	2 in.
maximum in total height 	-	3 in.

- Concrete support structure diameter variation -  	0.4% (not to exceed 3 in.)

- Dome floor radius variation	-	1.0%

- Level alignment variation:
from specified elevation	-	1 in.
from horizontal plane		-	1/2 in.

- The offset between adjacent pieces of formwork facing material shall not exceed the following:
Exterior exposed surfaces	-	1/8 in.
Interior exposed surfaces	-	1/4 in.
Unexposed surfaces		-	1/2 in.

  - FOUNDATION

    - Excavation
After verification of the foundation bearing surface, a 2 in. thick concrete working slab within the lower excavation limits may be provided.  Grade the site to prevent runoff from entering the excavation.

    - Finish
Formed surfaces shall have a smooth form finish when exposed and a rough form finish when not exposed.

  - FIELD QUALITY CONTROL

    - Concrete Testing and Inspection

- The evaluation and acceptance of concrete shall be in accordance with Section 5.6 of ACI 318 and ACI 117, except as modified in this Section.

- Three cylinders shall be made from each sample required.  A 7-day compressive strength test shall be used to supplement the 28 day tests.

- Slump, air, temperature and compressive cylinder testing shall be performed by an independent laboratory.  The Contractor shall retain the independent laboratory and provide the Contractor with copies of all test results.

- The concrete support structure radius, plumbness and thickness shall be verified for each concrete lift at 45 degree intervals.  An inspection report by the Contractor shall be provided to the Owner at project completion.

    - Welded Steel Water Tank Testing & Inspection

- Inspection procedures for the welded steel tank shall be as required by AWWA D107, Section 9, "Inspection and Testing".  Radiographic inspection of full penetration butt-welded joints shall be made by an independent inspection company retained by the Contractor.

- Conical sections of the welded steel water tank designed using Method 2 or Method 3 of AWWA D107 shall be inspected in accordance with Section 9.4 of AWWA D107.

- Weld joints of plate over the structural concrete floor shall be tested for leaks by vacuum box/soap solution testing, or equivalent method.